## 🔧 Pump Inspection
PUMP INSPECTION CHECKLIST
► ✓ = Satisfactory ✗ = Unsatisfactory — Action required N/A = Not applicable
Equipment Tag: |  |  |  | Pump Name / Description:
Date of Inspection: |  |  |  | Inspector:
Service (Fluid handled): |  |  |  | Work Order #:
# | Inspection Item | Specification / Limit | ✓/✗/N/A | Reading | Acceptable? | Action Required | Tech
MECHANICAL — GENERAL
1 | Check for visible leaks (gland, seal, casing joints) | No visible leakage
2 | Inspect paint / coating condition | No corrosion / blistering
3 | Check foundation bolts — tight | All bolts torqued
4 | Check grout condition | No cracking / settling
5 | Inspect mounting feet — level | Shim pack intact
BEARINGS & LUBRICATION
6 | Check bearing housing oil level | Within sight glass marks
7 | Check bearing temperature | ≤ 80°C (infrared)
8 | Measure bearing vibration — DE | ≤ 4.5 mm/s RMS (ISO 10816)
9 | Measure bearing vibration — NDE | ≤ 4.5 mm/s RMS
10 | Check grease nipple condition / grease fresh | As per lube schedule
11 | Listen for abnormal bearing noise | No grinding/clicking
MECHANICAL SEAL / GLAND PACKING
12 | Inspect seal flush line — flowing | Flow confirmed
13 | Check seal face leakage (mech. seal) | < 1 drop / min
14 | Check gland packing drip rate (if packed) | 3–5 drops / min
15 | Inspect seal pot level (double seals) | Above minimum
16 | Check buffer fluid pressure (double seals) | Per spec
IMPELLER & CASING
17 | Check discharge pressure | Per process P&ID
18 | Check suction pressure | Per process P&ID
19 | Calculate differential pressure | ΔP = discharge – suction
20 | Check flow rate vs design | Within ±10% of design
21 | Listen for cavitation noise | No rattling / crackling
22 | Check casing temperature | No unusual hot spots
COUPLING & ALIGNMENT
23 | Inspect coupling guard — in place & secured | Guarding intact
24 | Check coupling for wear / cracking | No visible wear
25 | Verify alignment within tolerance | ≤ 0.05 mm parallel, ≤ 0.05 mm angular
26 | Check coupling bolts / fasteners tight | All torqued
MOTOR
27 | Check motor winding temperature | < Insulation class limit
28 | Measure motor current (each phase) | Within nameplate FLA ±5%
29 | Check motor fan guard intact | Guarding in place
30 | Inspect motor terminal box — sealed | No moisture ingress
PIPEWORK & VALVES
31 | Inspect suction / discharge flanges — no leaks | Tight, no seepage
32 | Check suction valve — fully open | Open position confirmed
33 | Check discharge valve position | Per operating procedure
34 | Inspect pressure gauges — readable | Readable, needle in range
35 | Check flexible connections — condition | No cracking / swelling
INSTRUMENTATION
36 | Check pressure transmitter / gauge functioning | Reading stable
37 | Check flow meter indicating | Reading within spec
38 | Check temperature sensor | Reading plausible
OVERALL RESULT
Overall Status |  | SATISFACTORY / UNSATISFACTORY |  | Next Inspection Due |  | Inspector Signature