## 🔧 Pump Inspection
PUMP INSPECTION CHECKLIST
► ✓ = Satisfactory ✗ = Unsatisfactory — Action required N/A = Not applicable
Equipment Tag: |  |  |  | Pump Name / Description:
Date of Inspection: |  |  |  | Inspector:
Service (Fluid handled): |  |  |  | Work Order #:
# | Inspection Item | Specification / Limit | ✓/✗/N/A | Reading | Acceptable? | Action Required | Tech | Priority | Due Date | Action Status | Risk Score | Evidence Ref
MECHANICAL — GENERAL
1 | Check for visible leaks (gland, seal, casing joints) | No visible leakage
2 | Inspect paint / coating condition | No corrosion / blistering
3 | Check foundation bolts — tight | All bolts torqued
4 | Check grout condition | No cracking / settling
5 | Inspect mounting feet — level | Shim pack intact
BEARINGS & LUBRICATION
6 | Check bearing housing oil level | Within sight glass marks
7 | Check bearing temperature | ≤ 80°C (infrared)
8 | Measure bearing vibration — DE | ≤ 4.5 mm/s RMS (ISO 10816)
9 | Measure bearing vibration — NDE | ≤ 4.5 mm/s RMS
10 | Check grease nipple condition / grease fresh | As per lube schedule
11 | Listen for abnormal bearing noise | No grinding/clicking
MECHANICAL SEAL / GLAND PACKING
12 | Inspect seal flush line — flowing | Flow confirmed
13 | Check seal face leakage (mech. seal) | < 1 drop / min
14 | Check gland packing drip rate (if packed) | 3–5 drops / min
15 | Inspect seal pot level (double seals) | Above minimum
16 | Check buffer fluid pressure (double seals) | Per spec
IMPELLER & CASING
17 | Check discharge pressure | Per process P&ID
18 | Check suction pressure | Per process P&ID
19 | Calculate differential pressure | ΔP = discharge – suction
20 | Check flow rate vs design | Within ±10% of design
21 | Listen for cavitation noise | No rattling / crackling
22 | Check casing temperature | No unusual hot spots
COUPLING & ALIGNMENT
23 | Inspect coupling guard — in place & secured | Guarding intact
24 | Check coupling for wear / cracking | No visible wear
25 | Verify alignment within tolerance | ≤ 0.05 mm parallel, ≤ 0.05 mm angular
26 | Check coupling bolts / fasteners tight | All torqued
MOTOR
27 | Check motor winding temperature | < Insulation class limit
28 | Measure motor current (each phase) | Within nameplate FLA ±5%
29 | Check motor fan guard intact | Guarding in place
30 | Inspect motor terminal box — sealed | No moisture ingress
PIPEWORK & VALVES
31 | Inspect suction / discharge flanges — no leaks | Tight, no seepage
32 | Check suction valve — fully open | Open position confirmed
33 | Check discharge valve position | Per operating procedure
34 | Inspect pressure gauges — readable | Readable, needle in range
35 | Check flexible connections — condition | No cracking / swelling
INSTRUMENTATION
36 | Check pressure transmitter / gauge functioning | Reading stable
37 | Check flow meter indicating | Reading within spec
38 | Check temperature sensor | Reading plausible
OVERALL RESULT
Overall Status |  | SATISFACTORY / UNSATISFACTORY |  | Next Inspection Due |  | Inspector Signature

## Premium Guide
Pump Inspection Checklist — PREMIUM UPGRADE GUIDE
Original template preserved. Added premium sheets turn the file into a semi-automated maintenance management tool.
Step | What to do | Outcome
1 | Enter field data | Complete the original inspection/report sheet. Yellow cells and result columns are input fields.
2 | Use dropdowns | Use standardised results, priority, status, criticality and RCA decision fields to keep data clean.
3 | Review dashboard | Open the dashboard/summary sheet to view compliance, open actions, overdue actions and management risk indicators.
4 | Close actions | Transfer defects/recommendations to the Action Tracker with owner, due date, status and verification evidence.
5 | Issue report | Use the original form for site records and the added registers for meetings, audits and maintenance planning.
Upgrades Implemented
• Pump condition score and risk priority columns added to the inspection sheet.
• Pump performance sheet added for suction/discharge pressure, flow, current, head and operating point review.
• Trend log added for bearing temperature, vibration and seal leakage.
• Photo evidence log added for leaks, seals, coupling, base, corrosion and pipework defects.
• Dashboard added for compliance, defects, open actions and overdue actions.

## Lists
CONTROL LISTS / DROPDOWNS
Edit these lists if your site uses different status, priority, failure mode or criticality labels.
Status | Priority | Result | Severity | Failure Mode | Criticality | Shift | RCA Required
Open | Critical | ✓ | 1 | Mechanical | A - Critical | Day | Yes
In Progress | High | ✗ | 2 | Electrical | B - Important | Night | No
Complete | Medium | N/A | 3 | Lubrication | C - General | A | TBC
Overdue | Low | Monitor | 4 | Hydraulic |  | B
Deferred | Monitor |  | 5 | Pneumatic |  | C
Cancelled |  |  |  | Instrumentation |  | D
Verified |  |  |  | Process
Operator
Design
Unknown

## Action Tracker
ACTION TRACKER
Central register for defects, recommendations, close-out dates, and verification.
Source/Sheet | Asset / Equipment | Finding / Defect | Risk / Impact | Priority | Responsible Person | Due Date | Status | Close-out Date | Verification / Evidence | Days Overdue
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
[7 empty] | Open |  |  | 0
Formulas:
Days Overdue = IF(AND([Due Date]<>"",[Status]<>"Complete",[Status]<>"Verified"),MAX(0,TODAY()-[Due Date]),0)

## Defect Photo Log
DEFECT PHOTO LOG
Record photo evidence references; paste links to shared folders/CMMS records rather than inserting large images into the workbook.
Photo Ref | Pump Tag | Component / Location | Finding Shown | File/Folder Link | Taken By | Date | Severity | Action Ref | Notes
PH-001
PH-002
PH-003
PH-004
PH-005
PH-006
PH-007
PH-008
PH-009
PH-010
PH-011
PH-012
PH-013
PH-014
PH-015

## Pump Performance
PUMP PERFORMANCE CHECK
Compare actual operating readings with design values to identify cavitation, blockage, wear or off-design operation.
Date | Pump Tag | Fluid | Speed rpm | Suction Pressure | Discharge Pressure | Differential Pressure | Flow Rate | Motor Current | Design Flow | Design Head | Performance Status

## Condition Trend Log
CONDITION TREND LOG
Record readings over time to support trend-based maintenance and condition monitoring.
Date | Asset Tag | Operating Hours | Operating Condition | DE Temp (°C) | NDE Temp (°C) | DE Vib (mm/s) | NDE Vib (mm/s) | Seal Leak Rate | Motor Current (A) | Overall Status | Action Required | Technician

## Cavitation & Seal Checks
PUMP CAVITATION AND SEAL HEALTH CHECKS
Use these indicators to prioritise deeper pump investigation.
Indicator | Likely cause | Recommended check
Low suction pressure | Possible suction restriction / insufficient NPSH | Check suction valve, strainer, tank level and suction line
Crackling/gravel noise | Cavitation likely | Reduce flow restriction, check NPSH margin and pump speed
Vibration increase | Cavitation, misalignment, bearing wear or hydraulic imbalance | Trend vibration and inspect coupling/alignment
Seal leakage increase | Seal face wear, flush issue or pressure imbalance | Check seal flush, seal pot/barrier pressure and leakage rate
Flow drop with same speed | Impeller wear, blockage or suction problem | Check pump curve and inspect impeller/casing

## Premium Dashboard
PUMP INSPECTION DASHBOARD
Formula-driven summary from the inspection sheet and Action Tracker.
Metric | Value | Interpretation
Total checklist items | 38 | Numbered inspection items
Pass / OK count | 0 | All items marked satisfactory
Fail / defect count | 0 | Items requiring action
N/A count | 0 | Not applicable items
Compliance % | 0% | Passes ÷ applicable checks
Actions raised | 1 | Non-empty action fields
Open actions | 33 | Not complete or verified
Overdue actions | 32 | Past due and not complete
Overall status | OVERDUE ACTIONS | Management interpretation
Management Notes
Use this page before maintenance meetings to identify overdue actions, repeated failed items and repair priority.
Any defect without a responsible person and due date should be transferred to the Action Tracker.
Safety-critical failed items should trigger supervisor review before the equipment is returned to service.